## Item
Item Code | Description | Attribute (Variant Attributes) | Attribute Value (Variant Attributes)
DTTHZ2N 2000/20/6/125 | <b>2000 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 2340 [W], P(k) 16000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 2000
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 2340
|  | P(k)120°C (W) | 16000
|  | LWA (dB) | 69
DTTHZ2N 1600/20/6/125 | <b>1600 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1980 [W], P(k) 13000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1600
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 1980
|  | P(k)120°C (W) | 13000
|  | LWA (dB) | 67
DTTHZ2N 1250/20/6/125 | <b>1250 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1620 [W], P(k) 11000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 1620
|  | P(k)120°C (W) | 11000
|  | LWA (dB) | 66
DTTHZ2N 1000/20/6/125 | <b>1000 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1395 [W], P(k) 9000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1000
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 1395
|  | P(k)120°C (W) | 9000
|  | LWA (dB) | 64
DTTHZ2N 800/20/6/125 | <b>800 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1170 [W], P(k) 8000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 800
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 1170
|  | P(k)120°C (W) | 8000
|  | LWA (dB) | 63
DTTHZ2N 630/20/6/125 | <b>630 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 630/20/4/125 | <b>630 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 400/20/6/125 | <b>400 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 400/20/4/125 | <b>400 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 250/20/6/125 | <b>250 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 250/20/4/125 | <b>250 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 160/20/6/125 | <b>160 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 160/20/4/125 | <b>160 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 100/20/6/125 | <b>100 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50
DTTHZ2N 100/20/4/125 | <b>100 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 125
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50
DTTHZ2N 2500/20/6/95 | <b>2500 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 2790 [W], P(k) 19000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 2500
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 2790
|  | P(k)120°C (W) | 19000
|  | LWA (dB) | 70
DTTHZ2N 2000/20/6/95 | <b>2000 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 2340 [W], P(k) 16000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 2000
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 2340
|  | P(k)120°C (W) | 16000
|  | LWA (dB) | 69
DTTHZ2N 1600/20/6/95 | <b>1600 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1980 [W], P(k) 13000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1600
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 1980
|  | P(k)120°C (W) | 13000
|  | LWA (dB) | 67
DTTHZ2N 1250/20/6/95 | <b>1250 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1620 [W], P(k) 11000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 1620
|  | P(k)120°C (W) | 11000
|  | LWA (dB) | 66
DTTHZ2N 1000/20/6/95 | <b>1000 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1395 [W], P(k) 9000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1000
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 1395
|  | P(k)120°C (W) | 9000
|  | LWA (dB) | 64
DTTHZ2N 800/20/6/95 | <b>800 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 1170 [W], P(k) 8000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 800
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 1170
|  | P(k)120°C (W) | 8000
|  | LWA (dB) | 63
DTTHZ2N 630/20/6/95 | <b>630 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 630/20/4/95 | <b>630 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 400/20/6/95 | <b>400 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 400/20/4/95 | <b>400 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 250/20/6/95 | <b>250 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 250/20/4/95 | <b>250 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 160/20/6/95 | <b>160 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 160/20/4/95 | <b>160 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 100/20/6/95 | <b>100 [kVA], HV 20 [kV], LV 400 [V], uK 6 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50
DTTHZ2N 100/20/4/95 | <b>100 [kVA], HV 20 [kV], LV 400 [V], uK 4 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 20
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 95
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50
DTTHZ2N 2500/10/6/75 | <b>2500 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 2790 [W], P(k) 19000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 2500
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 2790
|  | P(k)120°C (W) | 19000
|  | LWA (dB) | 70
DTTHZ2N 2000/10/6/75 | <b>2000 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 2340 [W], P(k) 16000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 2000
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 2340
|  | P(k)120°C (W) | 16000
|  | LWA (dB) | 69
DTTHZ2N 1600/10/6/75 | <b>1600 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 1980 [W], P(k) 13000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1600
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 1980
|  | P(k)120°C (W) | 13000
|  | LWA (dB) | 67
DTTHZ2N 1250/10/6/75 | <b>1250 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 1620 [W], P(k) 11000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1250
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 1620
|  | P(k)120°C (W) | 11000
|  | LWA (dB) | 66
DTTHZ2N 1000/10/6/75 | <b>1000 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 1395 [W], P(k) 9000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 1000
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 1395
|  | P(k)120°C (W) | 9000
|  | LWA (dB) | 64
DTTHZ2N 800/10/6/75 | <b>800 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 1170 [W], P(k) 8000 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 800
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 1170
|  | P(k)120°C (W) | 8000
|  | LWA (dB) | 63
DTTHZ2N 630/10/6/75 | <b>630 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 630/10/4/75 | <b>630 [kVA], HV 10 [kV], LV 400 [V], uK 4 [%], P(0) 990 [W], P(k) 7100 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 630
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 990
|  | P(k)120°C (W) | 7100
|  | LWA (dB) | 61
DTTHZ2N 400/10/6/75 | <b>400 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 400/10/4/75 | <b>400 [kVA], HV 10 [kV], LV 400 [V], uK 4 [%], P(0) 675 [W], P(k) 4500 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 400
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 675
|  | P(k)120°C (W) | 4500
|  | LWA (dB) | 59
DTTHZ2N 250/10/6/75 | <b>250 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 250/10/4/75 | <b>250 [kVA], HV 10 [kV], LV 400 [V], uK 4 [%], P(0) 468 [W], P(k) 3400 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 250
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 468
|  | P(k)120°C (W) | 3400
|  | LWA (dB) | 56
DTTHZ2N 160/10/6/75 | <b>160 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 160/10/4/75 | <b>160 [kVA], HV 10 [kV], LV 400 [V], uK 4 [%], P(0) 360 [W], P(k) 2600 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 160
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 360
|  | P(k)120°C (W) | 2600
|  | LWA (dB) | 53
DTTHZ2N 100/10/6/75 | <b>100 [kVA], HV 10 [kV], LV 400 [V], uK 6 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 6
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50
DTTHZ2N 100/10/4/75 | <b>100 [kVA], HV 10 [kV], LV 400 [V], uK 4 [%], P(0) 252 [W], P(k) 1800 [W]</b><p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p> | POWER (kVA) | 100
|  | HV (kV) | 10
|  | LV (V) | 400
|  | IMP(%) | 4
|  | VECTOR GROUP | Dyn5
|  | LI (kV) | 75
|  | P(0) (W) | 252
|  | P(k)120°C (W) | 1800
|  | LWA (dB) | 50

## Item Description
Item Description
<p><br></p><p>This Transformer complies with the eco-design guidelines (according to EU 2009/125/EC) of the EU</p><p>parliament, inferential of EU regulation no. 548/214 from 21.05.2014 (Tier 2).</p><p><br></p><p>Transformers are equipped with:</p><p>- 1 set of bi-directional rollers</p><p>- 2 earthing points – M12</p><p>- 2nd rating plate (adhesive foil)</p><p>- SGB- standard documentation incl. routine test reports according to currently valid standards (IEC)</p><p>- 1 x PT100 sensor per phase</p>